## Compheat
Inputs are Yellow
Altitude = | 0 | FEET
Tin = | 70 | DEG F
Pin = | 0 | PSIG
Pout = | 100 | PSIG
CFM = | 1200
Absolute Atmospheric Pressure | 14.6805 | PSIA
single stage | 46.3488 | tons = | 556185.5757 | Btu/hr
two stage with intercooler | 43.3238 | tons = | 519886.0415 | Btu/hr
two stage without intercooler | 49.8542 | tons = | 598250.0433 | Btu/hr
temp at outlet of 1st stage = | 360.6539 | Deg F